## SE
|  | Note: | Tan cells are unlocked. Make all entries in these cells only. Use UPPERcase.
Move between tan cells using the Tab key or mouse. "Save-as" in the form "panelname.xls". For multi-pole breakers, enter the breaker trip size as "20 \" for 2-pole and "\ 20 \" for 3-pole. Copy or Ctrl-drag symbols to indicate receptacles and multi-pole breakers as shown; delete those not used. Import loads up to feeder panel. At bottom, delete color coding not used. Date is Mmm-yy. Only the colored section will print, in 8.5x11 landscape.
[6 empty] | 3 - PHASE PANEL SCHEDULE | SE | [5 empty] | LOCATION | South East | [6 empty] | BUILDING | Iceland |  |  | MAXIMO#
PANEL CHARACTERISTICS | [11 empty] | FEEDER INFORMATION | [12 empty] | REVISION LEVEL
| VOLTS | 240 | AMPS | 200 |  | WIRE |  | NEUTRAL |  |  |  | NO. OF WIRES AND SIZE |  |  |  |  | 4 3/0 CU |  |  |  |  | CONDUIT SIZE |  | 2" | DATE | BY | LETTER
| MFR |  | MODEL |  |  | MOUNTING |  | SURFACE |  |  |  | FEEDER SOURCE |  |  |  |  | MAIN SERVICE |  |  |  |  | ENTRANCE |  | BACK
| MAIN BREAKER FRAME |  |  |  | AMPS |  | LOCATION |  |  |  |  | FEEDER BREAKER FRAME | [9 empty] | XFMR KVA
| BRANCH BREAKER FRAME |  |  |  | KAIC | 10K | FAULT DUTY |  |  |  | KA | FEEDER CIRCUIT # | [5 empty] | AMPS | 200 |  |  | VOLTS |  | 240
| ARC-FLASH HAZARD CAT. |  |  |  | SPECIFICATIONS: PANELBOARD SHALL INCLUDE COPPER BUSES, GROUND BUS BONDED TO ENCLOSURE, NEMA R3 RATING,
PERMANENT LABELING, BE RATED FOR THE AVAILABLE FAULT DUTY AND MARKED FOR THE ARC-FLASH HAZARD CATEGORY.
ADDITIONAL NOTES:
R |  | CIRCUIT USE AND LOCATION | [7 empty] | BRANCH CHARACTERISTICS | [13 empty] | CIRCUIT USE AND LOCATION |  |  |  | R
E |  | SHOW FRAME SIZE IF OTHER THAN ABOVE | [7 empty] | LOAD AMPS |  |  | BKR | CKT |  | CKT | BKR | LOAD AMPS | [5 empty] | SHOW FRAME SIZE IF OTHER THAN ABOVE |  |  |  | E
V | SYMBOL | [8 empty] | A | B | C | TRIP | NO |  | NO | TRIP | A | B | C |  |  | SYMBOL |  |  |  |  | V
[10 empty] | 34 |  |  | 60 | 1 | A | 4 | 20 | 10 | [5 empty] | UTILITY RECEPTACLE 1
|  | NE PANELBOARD | [10 empty] | 60 | 2 | B | 5
[12 empty] | 30 | 60 | 3 | C | 6 | 20 |  |  | 10 |  |  |  | UTILITY RECEPTACLE 2
[10 empty] | 20 |  |  | 60 | 7 | A | 10 | 20 | 10 | [5 empty] | UTILITY RECEPTACLE 3
|  | SW PANEL BOARD | [10 empty] | 60 | 8 | B | 11
[12 empty] | 26 | 60 | 9 | C | 12 | 20 |  |  | 10 |  |  |  | UTILITY RECEPTACLE 4
|  | FLOOD LIGHTING 1 | [7 empty] | 10 |  |  | 20 | 13 | A | 16 | 20 | 10 | [5 empty] | OUTSIDE RECEPTACLE 1
[14 empty] | 14 | B | 17
|  | FLOOD LIGHTING 2 | [9 empty] | 10 | 20 | 15 | C | 18 | 20 |  |  | 10 |  |  |  | OUTSIDE RECEPTACLE 2
|  | PERIMETER LIGHTING 1 | [7 empty] | 5 |  |  | 20 | 19 | A | 22
[14 empty] | 20 | B | 23
|  | PERIMETER LIGHTING 2 | [9 empty] | 5 | 20 | 21 | C | 24
|  | EMERGENCY LIGHTING | [7 empty] | 1 |  |  | 20 | 25 | A | 28
[14 empty] | 26 | B | 29
[14 empty] | 27 | C | 30
[14 empty] | 31 | A | 34
[14 empty] | 32 | B | 35
[14 empty] | 33 | C | 36
[14 empty] | 37 | A | 40
[14 empty] | 38 | B | 41
[14 empty] | 39 | C | 42
| 120/208/240 VOLT COLOR CODING | [7 empty] | ^ | 70 | 0 | 71 |  | A | B | C |  | 30 | 0 | 30 | ^
| A-BLACK, B-RED, C-BLUE | [12 empty] | 100 | 0 | 101
| NEUTRAL-WHITE, GROUND-GREEN | [22 empty] | Printed: | 2026-07-29

## SW
|  | Note: | Tan cells are unlocked. Make all entries in these cells only. Use UPPERcase.
Move between tan cells using the Tab key or mouse. "Save-as" in the form "panelname.xls". For multi-pole breakers, enter the breaker trip size as "20 \" for 2-pole and "\ 20 \" for 3-pole. Copy or Ctrl-drag symbols to indicate receptacles and multi-pole breakers as shown; delete those not used. Import loads up to feeder panel. At bottom, delete color coding not used. Date is Mmm-yy. Only the colored section will print, in 8.5x11 landscape.
[6 empty] | 3 - PHASE PANEL SCHEDULE | SW | [5 empty] | LOCATION | SOUTH WEST | [6 empty] | BUILDING | Iceland |  |  | MAXIMO#
PANEL CHARACTERISTICS | [11 empty] | FEEDER INFORMATION | [12 empty] | REVISION LEVEL
| VOLTS | 240 | AMPS | 100 |  | WIRE | 3 | NEUTRAL |  | 1 |  | NO. OF WIRES AND SIZE |  |  |  |  | 4 #6 |  |  |  |  | CONDUIT SIZE |  | 2" | DATE | BY | LETTER
| MFR |  | MODEL |  |  | MOUNTING |  | SURFACE |  |  |  | FEEDER SOURCE |  |  |  |  | SE |  |  |  |  | ENTRANCE |  | BOTTOM
| MAIN BREAKER FRAME |  |  |  | AMPS |  | LOCATION |  |  |  |  | FEEDER BREAKER FRAME | [9 empty] | XFMR KVA
| BRANCH BREAKER FRAME |  |  |  | KAIC |  | FAULT DUTY |  |  |  | KA | FEEDER CIRCUIT # |  |  | 4, 5, 6 |  |  | AMPS | 60 |  |  | VOLTS |  | 240
| ARC-FLASH HAZARD CAT. |  |  |  | SPECIFICATIONS: PANELBOARD SHALL INCLUDE COPPER BUSES, GROUND BUS BONDED TO ENCLOSURE, NEMA R3 RATING,
PERMANENT LABELING, BE RATED FOR THE AVAILABLE FAULT DUTY AND MARKED FOR THE ARC-FLASH HAZARD CATEGORY.
ADDITIONAL NOTES:
R |  | CIRCUIT USE AND LOCATION | [7 empty] | BRANCH CHARACTERISTICS | [13 empty] | CIRCUIT USE AND LOCATION |  |  |  | R
E |  | SHOW FRAME SIZE IF OTHER THAN ABOVE | [7 empty] | LOAD AMPS |  |  | BKR | CKT |  | CKT | BKR | LOAD AMPS | [5 empty] | SHOW FRAME SIZE IF OTHER THAN ABOVE |  |  |  | E
V | SYMBOL | [8 empty] | A | B | C | TRIP | NO |  | NO | TRIP | A | B | C |  |  | SYMBOL |  |  |  |  | V
|  | UTILITY RECEPTACLE 1 | [7 empty] | 10 |  |  | 20 | 1 | A | 4
[14 empty] | 2 | B | 5
|  | UTILITY RECEPTACLE 2 | [9 empty] | 10 | 20 | 3 | C | 6
|  | UTILITY RECEPTACLE 3 | [7 empty] | 10 |  |  | 20 | 7 | A | 10
[14 empty] | 8 | B | 11
|  | UTILITY RECEPTACLE 4 | [9 empty] | 10 | 20 | 9 | C | 12
[14 empty] | 13 | A | 16
[14 empty] | 14 | B | 17
|  | SUMP PUMP | [9 empty] | 6 | 20 | 15 | C | 18
[14 empty] | 19 | A | 22
[14 empty] | 20 | B | 23
[14 empty] | 21 | C | 24
[14 empty] | 25 | A | 28
[14 empty] | 26 | B | 29
[14 empty] | 27 | C | 30
[14 empty] | 31 | A | 34
[14 empty] | 32 | B | 35
[14 empty] | 33 | C | 36
[14 empty] | 37 | A | 40
[14 empty] | 38 | B | 41
[14 empty] | 39 | C | 42
| 120/208/240 VOLT COLOR CODING | [7 empty] | ^ | 20 | 0 | 26 |  | A | B | C |  | 0 | 0 | 0 | ^
| A-BLACK, B-RED, C-BLUE | [12 empty] | 20 | 0 | 26
| NEUTRAL-WHITE, GROUND-GREEN | [22 empty] | Printed: | 2026-07-29

## NE
[6 empty] | 3 - PHASE PANEL SCHEDULE | NE | [5 empty] | LOCATION | NORTH EAST | [6 empty] | BUILDING | ICELAND |  |  | MAXIMO#
PANEL CHARACTERISTICS | [11 empty] | FEEDER INFORMATION | [12 empty] | REVISION LEVEL
| VOLTS | 240 | AMPS | 100 |  | WIRE | 3 | NEUTRAL |  | 1 |  | NO. OF WIRES AND SIZE |  |  |  |  | 4 #6 |  |  |  |  | CONDUIT SIZE |  | 1-1/2" | DATE | BY | LETTER
| MFR |  | MODEL |  |  | MOUNTING |  | SURFACE |  |  |  | FEEDER SOURCE |  |  |  |  | SE |  |  |  |  | ENTRANCE |  | BOTTOM
| MAIN BREAKER FRAME |  |  |  | AMPS |  | LOCATION |  |  |  |  | FEEDER BREAKER FRAME | [9 empty] | XFMR KVA
| BRANCH BREAKER FRAME |  |  |  | KAIC | 10K | FAULT DUTY |  |  |  | KA | FEEDER CIRCUIT # |  |  | 1, 2, 3 |  |  | AMPS | 60 |  |  | VOLTS |  | 240
| ARC-FLASH HAZARD CAT. |  |  |  | SPECIFICATIONS: PANELBOARD SHALL INCLUDE COPPER BUSES, GROUND BUS BONDED TO ENCLOSURE, NEMA R3 RATING,
PERMANENT LABELING, BE RATED FOR THE AVAILABLE FAULT DUTY AND MARKED FOR THE ARC-FLASH HAZARD CATEGORY.
ADDITIONAL NOTES:
R |  | CIRCUIT USE AND LOCATION | [7 empty] | BRANCH CHARACTERISTICS | [13 empty] | CIRCUIT USE AND LOCATION |  |  |  | R
E |  | SHOW FRAME SIZE IF OTHER THAN ABOVE | [7 empty] | LOAD AMPS |  |  | BKR | CKT |  | CKT | BKR | LOAD AMPS | [5 empty] | SHOW FRAME SIZE IF OTHER THAN ABOVE |  |  |  | E
V | SYMBOL | [8 empty] | A | B | C | TRIP | NO |  | NO | TRIP | A | B | C |  |  | SYMBOL |  |  |  |  | V
|  | NEON SIGN 1 | [7 empty] | 10 |  |  | 20 | 1 | A | 4 | 20 | 10 | [5 empty] | UTILITY RECEPTACLE 1
[14 empty] | 2 | B | 5
|  | NEON SIGN 2 | [9 empty] | 10 | 20 | 3 | C | 6 | 20 |  |  | 10 |  |  |  | UTILITY RECEPTACLE 2
|  | LED SIGNS | [7 empty] | 4 |  |  | 20 | 7 | A | 10 | 20 | 10 | [5 empty] | UTILITY RECEPTACLE 3
[14 empty] | 8 | B | 11
[14 empty] | 9 | C | 12 | 20 |  |  | 10 |  |  |  | UTILITY RECEPTACLE 4
[14 empty] | 13 | A | 16
[14 empty] | 14 | B | 17
[14 empty] | 15 | C | 18
[14 empty] | 19 | A | 22
[14 empty] | 20 | B | 23
[14 empty] | 21 | C | 24
[14 empty] | 25 | A | 28
[14 empty] | 26 | B | 29
[14 empty] | 27 | C | 30
[14 empty] | 31 | A | 34
[14 empty] | 32 | B | 35
[14 empty] | 33 | C | 36
[14 empty] | 37 | A | 40
[14 empty] | 38 | B | 41
[14 empty] | 39 | C | 42
| 120/208/240 VOLT COLOR CODING | [7 empty] | ^ | 14 | 0 | 10 |  | A | B | C |  | 20 | 0 | 20 | ^
| A-BLACK, B-RED, C-BLUE | [12 empty] | 34 | 0 | 30
| NEUTRAL-WHITE, GROUND-GREEN | [22 empty] | Printed: | 2026-07-29

## 3-Phase
|  | Note: | Tan cells are unlocked. Make all entries in these cells only. Use UPPERcase.
Move between tan cells using the Tab key or mouse. "Save-as" in the form "panelname.xls". For multi-pole breakers, enter the breaker trip size as "20 \" for 2-pole and "\ 20 \" for 3-pole. Copy or Ctrl-drag symbols to indicate receptacles and multi-pole breakers as shown; delete those not used. Import loads up to feeder panel. At bottom, delete color coding not used. Date is Mmm-yy. Only the colored section will print, in 8.5x11 landscape.
[6 empty] | 3 - PHASE PANEL SCHEDULE | SE | [5 empty] | LOCATION | South East | [6 empty] | BUILDING | Iceland |  |  | MAXIMO#
PANEL CHARACTERISTICS | [11 empty] | FEEDER INFORMATION | [12 empty] | REVISION LEVEL
| VOLTS | 240 | AMPS | 200 |  | WIRE |  | NEUTRAL |  |  |  | NO. OF WIRES AND SIZE | [9 empty] | CONDUIT SIZE |  |  | DATE | BY | LETTER
| MFR |  | MODEL |  |  | MOUNTING |  | SURFACE |  |  |  | FEEDER SOURCE | [9 empty] | ENTRANCE
| MAIN BREAKER FRAME |  |  |  | AMPS |  | LOCATION |  |  |  |  | FEEDER BREAKER FRAME | [9 empty] | XFMR KVA
| BRANCH BREAKER FRAME |  |  |  | KAIC |  | FAULT DUTY |  |  |  | KA | FEEDER CIRCUIT # | [5 empty] | AMPS |  |  |  | VOLTS
| ARC-FLASH HAZARD CAT. |  |  |  | SPECIFICATIONS: PANELBOARD SHALL INCLUDE COPPER BUSES, GROUND BUS BONDED TO ENCLOSURE, EXTENDED-WIDTH
SIDE GUTTERS, PERMANENT LABELING, BOLT-ON BREAKERS WITH DEVICES FOR LOCKING-OFF, PIANO-HINGED DOOR-IN-DOOR COVER, BE RATED FOR THE
AVAILABLE FAULT DUTY AND MARKED FOR THE ARC-FLASH HAZARD CATEGORY, AND SHALL MEET ALL PROVISIONS OF SANDIA SPECIFICATION 16440.
ADDITIONAL NOTES:
R |  | CIRCUIT USE AND LOCATION | [7 empty] | BRANCH CHARACTERISTICS | [13 empty] | CIRCUIT USE AND LOCATION |  |  |  | R
E |  | SHOW FRAME SIZE IF OTHER THAN ABOVE | [7 empty] | LOAD AMPS |  |  | BKR | CKT |  | CKT | BKR | LOAD AMPS | [5 empty] | SHOW FRAME SIZE IF OTHER THAN ABOVE |  |  |  | E
V | SYMBOL | [8 empty] | A | B | C | TRIP | NO |  | NO | TRIP | A | B | C |  |  | SYMBOL |  |  |  |  | V
[14 empty] | 1 | A | 4
[14 empty] | 2 | B | 5
[14 empty] | 3 | C | 6
[14 empty] | 7 | A | 10
[14 empty] | 8 | B | 11
[14 empty] | 9 | C | 12
[14 empty] | 13 | A | 16
[14 empty] | 14 | B | 17
[14 empty] | 15 | C | 18
[14 empty] | 19 | A | 22
[14 empty] | 20 | B | 23
[14 empty] | 21 | C | 24
[14 empty] | 25 | A | 28
[14 empty] | 26 | B | 29
[14 empty] | 27 | C | 30
[14 empty] | 31 | A | 34
[14 empty] | 32 | B | 35
[14 empty] | 33 | C | 36
[14 empty] | 37 | A | 40
[14 empty] | 38 | B | 41
[14 empty] | 39 | C | 42
| 120/208 VOLT COLOR CODING | [7 empty] | ^ | 0 | 0 | 0 |  | A | B | C |  | 0 | 0 | 0 | ^ | 277/480 COLOR CODING
| A-BLACK, B-RED, C-BLUE | [12 empty] | 0 | 0 | 0 | [5 empty] | A-BROWN, B-ORANGE, C-YELLOW
| NEUTRAL-WHITE, GROUND-GREEN | [8 empty] | * PROVIDE AND INSTALL NEW BREAKER * | [11 empty] | NEUTRAL-GRAY, GROUND-GREEN W/YELLOW TRACER
[12 empty] | Panel Template modified Oct 08 by Hoe | [11 empty] | Printed: | 2026-07-29
q
ac51