## takeoff
ITEM		USE	SIZE	NUMBER OF	TYPE	LENGTH (ft) or		Rob's notes
1/2/2011 supersedes 12/29/10				CONDUTORS		quantity
				(Cu)
1	Drop for SMUD to metered fused Main disconnect (item 2a)			4	THHN/THWN	12		I don't know if we supply this or if SMUD does.
2a	Meter Socket, 3 phase		200 Amp	NEMA 3R	Smud type with test bypass	1		Does this need to be nema 4 or nema 3R?
2b	combined with item 2a & 2c		n/a	n/a	n/a	n/a
2c	Switch, Main power disconnect switch (200A, 240VAC, 3phase )		NEMA 3R	5 feed	200A,240vac3phase	1
2d	wire, Ground wire for main disconnect		#2	1	Solid bare	50 ft
2e	Conduit, Ground conduit for main disconnect		3/4 in	1	EMT	50 ft
2f	wire, SMUD connection point to meter socket		3/0 awg	4	THHN/THWN	20' ea		guessing on the length
2g	wire, meter socket to disconnect switch to SE panel		3/0 awg	4	THHN/THWN	15'		guessing on the length
2h	wire, ground between iceland and american ice		#2 awg	1	bare	100'		guessing on the length
3	Conduit, Connect Main power distrubution pnl to distrubution pnl "SW"		2 in		EMT	1
4	Panel, Main power distrubution panel "SE" (200A, 240VAC, 3phase,4wire )		NEMA 3R	42 circ	200A,240vac3phase	1
4a	Bkrs for panel "SE"		60A		60A, 3P	2
4b	Bkrs for panel "SW", GFI		20A		20A, 1P	11		I think we only need 5 for SW, but we need 4 on SE and 4 on NE
5	Conduit from existing 2in rigid conduit to new 2in EMT		2in		PVC	60 ft
5a	Conduit from new 2in PVC up to new panel "NE"		2in		EMT	10 ft		can this be 2" or does it have to match the 1-1/2" that it connects to?
6	Wire from pnl "SE" to pnl "SW"		#6 AWG	5	THHN/THWN	150 ft		I think we only need #6 for 60 amp
7	Panel "SW" Located inside back of rink nr. Rear exit (125A, 240VAC,3phase)		NEMA 3R	42 Circuit	125A,240VAC,3phase	1
7a	Bkrs for panel "SW", GFI		20A		20A, 1P	5
8	Wire from pnl "SE" to pnl "NE"		#6 AWG	5	THHN/THWN	160 ft
9	Conduit from existing 1-1/2in rigid conduit to new 1-1/2in EMT		1-1/2in	5 #6AWG	PVC	40 ft
10	Panel "NE" Located inside front of rink nr. Front exit (125A, 240VAC,3phase)		NEMA 3R	42 Circuit	125A,240VAC,3phase	1
10a	Bkrs for panel "NE", GFI		20A		20A, 1P	7
11	Conduit from new 1-1/2in 1-1/2 PVC up to new panel "NE"		1-1/2in	5 #6AWG	EMT	10 ft
12	wire, Gas pipe ground wire		#6AWG	1	solid bare	20 ft
13	Conduit, Gas pipe conduit from pnl "NE" to gas pipe		3/4 in	1	EMT	20 ft
13a	wire, Gas pipe ground wire pipe connector		3/4 in	1	pipe to wire connector	1
14	wire, Water pipe ground		#6	1	solid bare	180 ft
15a	Conduit, Water pipe ground wire conduit from 3/4 in EMT to water pipe		3/4 in	1	PVC	30 ft
15	Conduit, Water pipe ground wire conduit from pnl "SW" to 3/4 in PVC (item 16)		3/4 in	1	EMT	30 ft
16	Wire, Water pipe ground wire pipe connector		3/4 in	1	pipe to wire connector	1
17	Anchors for power panels "SW", "SE", "NE"		1/2 in		"red heads"	16
18	Anchors for 2" EMT (conduit clamps for concrete)		2 in		std 2" EMT	1 doz
19	Anchors for 1-1/2" EMT (for conduit clamps for concrete)		1-1/2 in		std 1-1/2 EMT	1 doz
20	Anchors for 3/4 " EMT ( for conduit clamps for concrete)		3/4 in		std 3/4 EMT	4 doz
21	Lighting, Exit "XL" , Greentorch XWLC				Greentorch XWLC	2		in-stock
22	Lighting, Exit "EL" , Greentorch WVHEL				Greentorch WVHEL	3		ordered
23	Lighting, Outdoor light "OL", wall pack-e-conolight E-WP1F421Z				Econolight E-WP1F421Z	8		in-stock
24	Lighting, Flood light "FL" pole mount, item 46 for poles				Econolight E-HR4P25QZ	5		in-stock
25	Junction box "j", 4x4 or 8x8?		4x4		?	14
26	Lighting, switch box , 3 gang, rink perimeter lighting inside.		3 gang		3 gang, weathertight, 3/4"	1
27	Lighting, switch box, 1 gang, rink perimeter lighting outside.		duplex		1 gang, weathertight, 3/4"	1
28	Lighting, switch box, 2 gang, "ICELAND" lighting and pagoda control box.		quad		2 gang, weathertight, 3/4"	1
29	Conduit, 3/4" EMT, 40 ft from panel "NE" to sign switch (item 28)		3/4"		EMT	40 ft
30	Wire, #12AWG Cu, THHN/THWN, black, sign power from pnl "NE".		#12 AWG	1	#12AWG THHN/THWN	40 ft
31	Wire, #12AWG Cu, THHN/THWN,white, sign power from pnl "NE".		#12 AWG	1	#12AWG THHN/THWN	40 ft
32	Wire, #12AWG Cu, THHN/THWN, green, sign power from pnl "NE".		#12 AWG	1	#12AWG THHN/THWN	40 ft
33	Receptical box, 4x4, weather tight, power from pnl "SW". See item 52		#12 AWG		4X4, weathertight, 3/4"	2
34	Receptical box, 2x2, weather tight, power from pnl "SW".		#12 AWG		2x2, weathertight, 3/4"	1
35	Conduit, 3/4" SCH40 PVC, to item 34		3/4"		SCH40, PVC	40 ft
36	Wire, #12AWG Cu, THHN/THWN, black, sign power from pnl "SW".		#12 AWG	1	#12AWG THHN/THWN	40 ft
37	Wire, #12AWG Cu, THHN/THWN,white, sign power from pnl "SW".		#12 AWG	1	#12AWG THHN/THWN	40 ft
38	Wire, #12AWG Cu, THHN/THWN, green, sign power from pnl "SW".		#12 AWG	1	#12AWG THHN/THWN	40 ft
39	Conduit, 3/4" EMT, power from 4x4 box switch to all "FL", NE side, 2 runs of 120 ft.		#12 AWG		EMT	240 ft
40	Conduit, 3/4" EMT, power from 4x4 box switch to all "FL", SW side, 2 runs of 80 ft.		#12 AWG		EMT	160 ft
41	Wire, #12AWG Cu, THHN/THWN, black, power for "FL", 2 runs of 200 ft.		#12 AWG	1	#12AWG THHN/THWN	400 ft
42	Wire, #12AWG Cu, THHN/THWN, white, power for "FL", 2 runs of 200 ft.		#12 AWG	1	#12AWG THHN/THWN	400 ft
43	Wire, #12AWG Cu, THHN/THWN, green, power for "FL", 2 runs of 200 ft.		#12 AWG	1	#12AWG THHN/THWN	400 ft
44	Nipples, 2", for box entry items 2c,47		3/4 in		3/4" EMT compression type	12
45	Couplers, 3/4" for connection of 3/4"conduit, items 29,35,39 & 40		3/4 in		3/4" EMT compression type	50
46	Lighting, poles for "FL" (item 24)		2" dia		2" dia steel, 20 ft long (water pipe)	5		These can be rigid conduit or water pipe. The actual OD is 2-3/8", I think. Water is probably easier.
47	Lighting, pole bracing kits		2"			5		These are the brace kits that normally go on periscope service inlets.
48	Nipples, 1-1/2", for box entry on items 10 &4		1-1/2 in		1-1/2 compression type	2
49	Nipples, 3/4" for box entry items 7,10,4,29,34,35,36,37,38,39,40,41,42,43		3/4"		3/4" compression type	100
50	Conduit, 1" EMT, from LED sign switch to sign		1"		EMT	10 ft
51	Receptical box, weathertight, 3/4" entry. See item 33				2x2, weathertight, 3/4"	12
52	Receptical box, weathertight, 3/4" entry. Outside 4x4 nr "SVC"				4X4, weathertight, 3/4"	1
53	Unistrut for attaching panels "SVC", "SE", "SW", & "NE"				20 ft unistrut	20 ft
54	Flex, 3/4 weathertight, for connection frm "J" to "FL"s, "XL"s &"EL"s				30 feet	30 ft
55	Conduit " Jakes" for flex fittings, item54				EMT	4 doz
56	Conduit, 1/2", EMT, conncetion from "J" to "FL"				EMT	50 ft
57	6" x 6" x 48" or 60" NEMA 3R gutter for SE wall between SE panel and conduits
58	copper ground bus for american ice, approx. 12 - 16" long
59	box for ground bus at american ice

## summary
ITEM	USE	SIZE	Qty x Len	Description	Total		Rob's notes
	200 A, 240 V safety switch with 200 A fuses for #2
	600 V 100 A fuses for Chiller #2 disconnect.
	Anchor	1/4”		hammer type	50
	Anchor	1/2 in		sleeve anchor	20
	Anchor	1/4”		wedge anchor	50
	Breaker, Square D, QO	20A		20A, 1P	8
	Breaker, Square D, QO	60A		60A, 3P	2
	Breaker, Square D, QO	20A		20A, 1P, gfi	11
	box	6 x 6”	18”	gutter	1		ground point at American Ice
	box , 3 gang, rink perimeter lighting inside.			3 gang, weathertight, 3/4"	1
	box, "j", 4x4 or 8x8?	4x4		?	14
	box, 1 gang, rink perimeter lighting outside.			1 gang, weathertight, 3/4"	1
	box, 2 gang, "ICELAND" lighting and pagoda control box.			2 gang, weathertight, 3/4"	1
	Box, 6" x 6" x 48" or 60" NEMA 3R gutter for SE wall between SE panel and conduits
	Box, receptacle, 2x2, weather tight, power from pnl "SW".			2x2, weathertight, 3/4"	1
	Box, Receptical, weathertight, 3/4" entry. Outside 4x4 nr "SVC"			4X4, weathertight, 3/4"	1
	Box, receptical, weathertight, 3/4" entry. See item 33			2x2, weathertight, 3/4"	12
	Box, Recepticle, 4x4, weather tight, power from pnl "SW". See item 52			4X4, weathertight, 3/4"	2
	brace kit	2” grc post	6		6
	clamp	1-1/2”		strut-type	10
	clamp	2”		strut-type	?
	clamp	4”		strut-type	8
	Conduit	1-1/2in		EMT	10 ft
	Conduit	1"		EMT	10 ft
	Conduit	1/2”		EMT	50 ft		from “J” to “FL”,
	Conduit	2in		EMT	10 ft		can this be 2" or does it have to match the 1-1/2" that it connects to?
	Conduit	3/4"		EMT	600 ft		40 ft from panel "NE" to sign switch (item 28)
	Conduit	1-1/2in		PVC	40 ft
	Conduit	2in		PVC	60 ft
	Conduit	3/4"		PVC	200 ft
	Conduit, Connect Main power distrubution pnl to distrubution pnl "SW"	2 in		grc	10”
	Conduit, Flex, 3/4 weathertight, for connection frm "J" to "FL"s, "XL"s &"EL"s			30 feet	30 ft
	Connector	1-1/2 in		1-1/2 compression type	2
	connector	3/4"		3/4" compression type, emt	60
	connector	2”		compression type, outdoor	2
	Connector	1/2”		EMT	60		jakes for flex fittings
	Connector	1-1/2”	1	grc	1
	Connector	2”	1	grc	1
	copper ground bus for american ice, approx. 12 - 16" long
	FA, PVC, 1-1/2”		4	to steel connector	4
	FA, PVC, 2”		4		4
	Lighting, Exit "EL" , Greentorch WVHEL			Greentorch WVHEL	3		ordered
	Lighting, Exit "XL" , Greentorch XWLC			Greentorch XWLC	2		in-stock
	Lighting, Flood light "FL" pole mount, item 46 for poles			Econolight E-HR4P25QZ	5		in-stock
	Lighting, Outdoor light "OL", wall pack-e-conolight E-WP1F421Z			Econolight E-WP1F421Z	8		in-stock
	Lighting, poles for "FL" (item 24)	2" dia		2" dia steel, 20 ft long (water pipe)	5		These can be rigid conduit or water pipe. The actual OD is 2-3/8", I think. Water is probably easier.
	Load center, Panel "NE"	NEMA 3R	30 Circuit	125A,240VAC,3phase	1
	Load Center, Panel "SE"	NEMA 3R	42 circ	200A,240vac3phase	1
	Load Center, Panel "SW"	NEMA 3R	30 Circuit	125A,240VAC,3phase	1
	lugs, 1/4” bolt hole, fit #2 - #12 minimum		24
	Meter Socket, 3 phase	200 Amp	NEMA 3R	Smud type with test bypass	1
	meyer hubs	3/4”			60
	nipple, 2” grc	2”	10”	nipple from gutter to outside box	10”
	nipple, 2” grc		2' 4” +	threaded nipple
	Safety Switch, Main power disconnect switch (200A, 240VAC, 3phase )	NEMA 3R	5 feed	200A,240vac3phase	1
	strap	3/4”		1 hole strap	80
	sweep	2”		grc	1
	unistrut, galvanized	1” x 10'	3	10' shallow strut	3
	Wire from pnl "SE" to pnl "NE"	#6 AWG	5	THHN/THWN	160 ft
	Wire from pnl "SE" to pnl "SW"	#6 AWG	5	THHN/THWN	150 ft		I think we only need #6 for 60 amp
	Wire, #12AWG Cu, THHN/THWN, black, power for "FL", 2 runs of 200 ft.	#12 AWG	1	#12AWG THHN/THWN	400 ft
	Wire, #12AWG Cu, THHN/THWN, black, sign power from pnl "NE".	#12 AWG	1	#12AWG THHN/THWN	40 ft
	Wire, #12AWG Cu, THHN/THWN, black, sign power from pnl "SW".	#12 AWG	1	#12AWG THHN/THWN	40 ft
	Wire, #12AWG Cu, THHN/THWN, green, power for "FL", 2 runs of 200 ft.	#12 AWG	1	#12AWG THHN/THWN	400 ft
	Wire, #12AWG Cu, THHN/THWN, green, sign power from pnl "NE".	#12 AWG	1	#12AWG THHN/THWN	40 ft
	Wire, #12AWG Cu, THHN/THWN, green, sign power from pnl "SW".	#12 AWG	1	#12AWG THHN/THWN	40 ft
	Wire, #12AWG Cu, THHN/THWN, white, power for "FL", 2 runs of 200 ft.	#12 AWG	1	#12AWG THHN/THWN	400 ft
	Wire, #12AWG Cu, THHN/THWN,white, sign power from pnl "NE".	#12 AWG	1	#12AWG THHN/THWN	40 ft
	Wire, #12AWG Cu, THHN/THWN,white, sign power from pnl "SW".	#12 AWG	1	#12AWG THHN/THWN	40 ft
	wire, Gas pipe ground wire	#6AWG	1	solid bare	20 ft
	wire, Gas pipe ground wire pipe connector	3/4 in	1	pipe to wire connector	1
	wire, ground between iceland and american ice	#2 awg	1	bare	100'		estimated
	wire, Ground wire for main disconnect	#2	1	Solid bare	50 ft
	wire, meter socket to disconnect switch to SE panel	3/0 awg	4	THHN/THWN	15'		guessing on the length
	wire, SMUD connection point to meter socket	3/0 awg	4	THHN/THWN	20' ea		guessing on the length
	wire, Water pipe ground	#6	1	solid bare	180 ft
	Wire, Water pipe ground wire pipe connector	3/4 in	1	pipe to wire connector	1

## Hi-Line order, 2-4-11
ITEM	USE	SIZE	Length	Description	Total		Notes
1	box	6 x 6”	18”	gutter	1
2	brace kit	2” grc post			6
3	clamp	1-1/2”		strut-type	10
4	clamp	4”		strut-type	8
5	Conduit	1-1/2in		EMT	10 ft
6	Conduit	1-1/2in		PVC	40 ft
7	Conduit	1/2”		EMT	50 ft
8	Conduit	2in		PVC	60 ft
9	Conduit	3/4"		EMT	600 ft
10	Conduit	3/4"		PVC	200 ft
11	Connector	1-1/2”		ridig	1
13	Connector	2”		rigid	1
14	connector	3/4"		3/4" compression type, emt	60
15	FA, PVC, 1-1/2”			to steel connector	4
16	FA, PVC, 2”				4
17	Lighting, poles for "FL" (item 24)	2" dia		2" dia steel, 20 ft long (water pipe)	5		These can be rigid conduit or water pipe. The actual OD is 2-3/8".
18	Load center, Panel "NE"	NEMA 3R	30 Circuit	125A,240VAC,3phase	1		Square D QO
19	Load Center, Panel "SW"	NEMA 3R	30 Circuit	125A,240VAC,3phase	1		Square D QO
20	lugs	#2 - #12		1 barrel, bolt on	24		need to fit a 1/4” bolt hole
21	meyer hub	2”			4
22	meyer hubs	3/4”			60
23	nipple, 2” grc	2”	10”	threaded rigid nipple	10”
24	nipple, 2” grc		2' 4” +	threaded rigid nipple			should be this or longer.
25	strap	3/4”		1 hole strap	80
26	sweep	2”		rigid sweep, threaded	1
27	unistrut, galvanized	1” x 10'	3	10' shallow strut	3
28	service entrance weatherhead	2”		commercial type	1
	American Iceland Order
	Contact: Rob Kerth
	916-799-3121