## Wire Size Calculator
Temperature rating		90	C
Conductors in conduit		5
Outside Max Temperature		95	F

Size		Wire Capacity	Fill Correction	Temperature Correction	error		90	75	60		20	9	6	3		0	87	96	105	114	123	132	141		60	2		60
250	223	290	0.8	0.96	0		290	255	215		0.5	0.7	0.8	1	60	1	0.91	0.82	0.71	0.58	0.41	0	0		75	3
4/0	200	260	0.8	0.96	0		260	230	195		0.5	0.7	0.8	1	75	1	0.94	0.88	0.82	0.75	0.67	0.58	0.33		90	4
3/0	173	225	0.8	0.96	0		225	200	165		0.5	0.7	0.8	1	90	1	0.96	0.91	0.87	0.82	0.76	0.71	0.58
2/0	150	195	0.8	0.96	0		195	175	145		0.5	0.7	0.8	1
1/0	131	170	0.8	0.96	0		170	150	125		0.5	0.7	0.8	1
1	115	150	0.8	0.96	0		150	130	110		0.5	0.7	0.8	1
2	100	130	0.8	0.96	0		130	115	95		0.5	0.7	0.8	1
3	84	110	0.8	0.96	0		110	100	85		0.5	0.7	0.8	1
4	73	95	0.8	0.96	0		95	85	70		0.5	0.7	0.8	1
6	58	75	0.8	0.96	0		75	65	55		0.5	0.7	0.8	1
8	42	55	0.8	0.96	0		55	50	40		0.5	0.7	0.8	1
10	31	40	0.8	0.96	0		40	35	30		0.5	0.7	0.8	1
12	23	30	0.8	0.96	0		30	25	25		0.5	0.7	0.8	1
14	19	25	0.8	0.96	0		25	20	20		0.5	0.7	0.8	1

## Definitions
Wire conductor area
AWG	Area
250
4/0	0.3237
3/0	0.2679
2/0	0.2223
0	0.1855
1	0.1562
2	0.1158
3	0.0973
4	0.0824
6	0.0507
8	0.0366
10	0.0211
12	0.0133
14	0.0111

Fill Allowances
EMT	sq in	size
1 conductor	-0.100	1/2
53% fill	0.161	3/4
	0.283	1
	0.458	1 1/4
	0.793	1 1/2
	1.079	2
	1.778	2 ½
	3.105	3
	4.688	3-1/2
	6.119	4
	7.819	4+

2 conductors	-0.100	1/2
31% fill	0.094	3/4
	0.165	1
	0.268	1 1/4
	0.464	1 1/2
	0.631	2
	1.040	2 ½
	1.816	3
	2.742	3-1/2
	3.579	4
	4.573	4+

3 or more conductors	-0.100	1/2
40% fill	0.122	3/4
	0.213	1
	0.346	1 1/4
	0.598	1 1/2
	0.814	2
	1.342	2 ½
	2.343	3
	3.538	3-1/2
	4.618	4
	5.901	4+

## EMT Fill Calculator
Misc	Total
Number of Conductors	5	4	1	0	0	0	0	0	0	0
AWG		3/0	6	2/0	12	12	12	12	12	12
Area	1.1223	1.0716	0.0507	0.0000	0.0000	0.0000	0.0000	0.0000	0.0000	0.0000

Pipe required	2

Panel A Circuits	Total
Number of Conductors	5	4	1
AWG		1	6	10	12	12	12	12	12	12
Area	0.6755	0.6248	0.0507	0.0000	0.0000	0.0000	0.0000	0.0000	0.0000	0.0000

Pipe required	1 1/2

## EMT
EMT Conduit & Fittings
		1/2	3/4	1	1 1/4	1 1/2	2
	Connectors	0	0	0	37	0	0
	couplings	0	0	0	1	0	0
	bushings	0	0	0	25	0	0
	nuts	0	0	0	0	0	0
	pipe	0	0	0	68	0	0
	LB	0	0	0	11	0	0
	SLB	0	0	0	0	0	0
	chase nipple	0	0	0	5	0	0
	b	0	0	0	0	0	0
	c	0	0	0	0	0	0
	d	0	0	0	0	0	0
	e	0	0	0	0	0	0
	f	0	0	0	0	0	0
	g	0	0	0	0	0	0
	h	0	0	0	0	0	0
	I	0	0	0	0	0	0
	j	0	0	0	0	0	0

Panel B		Size	Quantity					1/2	3/4	1	1 1/4	1 1/2	2
	Connectors	1 1/4	4					0	0	0	4	0	0
	couplings					0	0	0	0	0	0
	bushings	1 1/4	4					0	0	0	4	0	0
	nuts					0	0	0	0	0	0
	pipe	1 1/4	6					0	0	0	6	0	0
	LB					0	0	0	0	0	0
	SLB					0	0	0	0	0	0
	chase nipple					0	0	0	0	0	0
	b					0	0	0	0	0	0
	c					0	0	0	0	0	0
	d					0	0	0	0	0	0
	e					0	0	0	0	0	0
	f					0	0	0	0	0	0
	g					0	0	0	0	0	0
	h					0	0	0	0	0	0
	I					0	0	0	0	0	0
	j					0	0	0	0	0	0

Panel C		Size	Quantity					1/2	3/4	1	1 1/4	1 1/2	2
	Connectors	1 1/4	4					0	0	0	4	0	0
	couplings	1 1/4					0	0	0	0	0	0
	bushings	1 1/4	2					0	0	0	2	0	0
	nuts	1 1/4					0	0	0	0	0	0
	pipe	1 1/4	8					0	0	0	8	0	0
	LB	1 1/4	2					0	0	0	2	0	0
	SLB	1 1/4					0	0	0	0	0	0
	chase nipple	1 1/4	1					0	0	0	1	0	0
	b	1 1/4					0	0	0	0	0	0
	c	1 1/4					0	0	0	0	0	0
	d	1 1/4					0	0	0	0	0	0
	e	1 1/4					0	0	0	0	0	0
	f	1 1/4					0	0	0	0	0	0
	g	1 1/4					0	0	0	0	0	0
	h	1 1/4					0	0	0	0	0	0
	I	1 1/4					0	0	0	0	0	0
	j	1 1/4					0	0	0	0	0	0

Panel D		Size	Quantity					1/2	3/4	1	1 1/4	1 1/2	2
	Connectors	1 1/4	8					0	0	0	8	0	0
	couplings	1 1/4					0	0	0	0	0	0
	bushings	1 1/4	4					0	0	0	4	0	0
	nuts	1 1/4					0	0	0	0	0	0
	pipe	1 1/4	14					0	0	0	14	0	0
	LB	1 1/4	2					0	0	0	2	0	0
	SLB	1 1/4					0	0	0	0	0	0
	chase nipple	1 1/4					0	0	0	0	0	0
	b	1 1/4					0	0	0	0	0	0
	c	1 1/4					0	0	0	0	0	0
	d	1 1/4					0	0	0	0	0	0
	e	1 1/4					0	0	0	0	0	0
	f	1 1/4					0	0	0	0	0	0
	g	1 1/4					0	0	0	0	0	0
	h	1 1/4					0	0	0	0	0	0
	I	1 1/4					0	0	0	0	0	0
	j	1 1/4					0	0	0	0	0	0

Panel 1		Size	Quantity					1/2	3/4	1	1 1/4	1 1/2	2
	Connectors	1 1/4	8					0	0	0	8	0	0
	couplings	1 1/4					0	0	0	0	0	0
	bushings	1 1/4	8					0	0	0	8	0	0
	nuts	1 1/4					0	0	0	0	0	0
	pipe	1 1/4	15					0	0	0	15	0	0
	LB	1 1/4	2					0	0	0	2	0	0
	SLB	1 1/4					0	0	0	0	0	0
	chase nipple	1 1/4	2					0	0	0	2	0	0
	b	1 1/4					0	0	0	0	0	0
	c	1 1/4					0	0	0	0	0	0
	d	1 1/4					0	0	0	0	0	0
	e	1 1/4					0	0	0	0	0	0
	f	1 1/4					0	0	0	0	0	0
	g	1 1/4					0	0	0	0	0	0
	h	1 1/4					0	0	0	0	0	0
	I	1 1/4					0	0	0	0	0	0
	j	1 1/4					0	0	0	0	0	0

Panel 2		Size	Quantity					1/2	3/4	1	1 1/4	1 1/2	2
	Connectors	1 1/4	13					0	0	0	13	0	0
	couplings	1 1/4	1					0	0	0	1	0	0
	bushings	1 1/4	7					0	0	0	7	0	0
	nuts	1 1/4					0	0	0	0	0	0
	pipe	1 1/4	25					0	0	0	25	0	0
	LB	1 1/4	5					0	0	0	5	0	0
	SLB	1 1/4					0	0	0	0	0	0
	chase nipple	1 1/4	2					0	0	0	2	0	0
	b	1 1/4					0	0	0	0	0	0
	c	1 1/4					0	0	0	0	0	0
	d	1 1/4					0	0	0	0	0	0
	e	1 1/4					0	0	0	0	0	0
	f	1 1/4					0	0	0	0	0	0
	g	1 1/4					0	0	0	0	0	0
	h	1 1/4					0	0	0	0	0	0
	I	1 1/4					0	0	0	0	0	0
	j	1 1/4					0	0	0	0	0	0

Panel A		Size	Quantity					1/2	3/4	1	1 1/4	1 1/2	2
	Connectors					0	0	0	0	0	0
	couplings					0	0	0	0	0	0
	bushings					0	0	0	0	0	0
	nuts					0	0	0	0	0	0
	pipe					0	0	0	0	0	0
	LB					0	0	0	0	0	0
	SLB					0	0	0	0	0	0
	chase nipple					0	0	0	0	0	0
	b					0	0	0	0	0	0
	c					0	0	0	0	0	0
	d					0	0	0	0	0	0
	e					0	0	0	0	0	0
	f					0	0	0	0	0	0
	g					0	0	0	0	0	0
	h					0	0	0	0	0	0
	I					0	0	0	0	0	0
	j					0	0	0	0	0	0

Panel A		Size	Quantity					1/2	3/4	1	1 1/4	1 1/2	2
	Connectors					0	0	0	0	0	0
	couplings					0	0	0	0	0	0
	bushings					0	0	0	0	0	0
	nuts					0	0	0	0	0	0
	pipe					0	0	0	0	0	0
	LB					0	0	0	0	0	0
	SLB					0	0	0	0	0	0
	chase nipple					0	0	0	0	0	0
	b					0	0	0	0	0	0
	c					0	0	0	0	0	0
	d					0	0	0	0	0	0
	e					0	0	0	0	0	0
	f					0	0	0	0	0	0
	g					0	0	0	0	0	0
	h					0	0	0	0	0	0
	I					0	0	0	0	0	0
	j					0	0	0	0	0	0

Panel A		Size	Quantity					1/2	3/4	1	1 1/4	1 1/2	2
	Connectors					0	0	0	0	0	0
	couplings					0	0	0	0	0	0
	bushings					0	0	0	0	0	0
	nuts					0	0	0	0	0	0
	pipe					0	0	0	0	0	0
	LB					0	0	0	0	0	0
	SLB					0	0	0	0	0	0
	chase nipple					0	0	0	0	0	0
	b					0	0	0	0	0	0
	c					0	0	0	0	0	0
	d					0	0	0	0	0	0
	e					0	0	0	0	0	0
	f					0	0	0	0	0	0
	g					0	0	0	0	0	0
	h					0	0	0	0	0	0
	I					0	0	0	0	0	0
	j					0	0	0	0	0	0

Panel A		Size	Quantity					1/2	3/4	1	1 1/4	1 1/2	2
	Connectors					0	0	0	0	0	0
	couplings					0	0	0	0	0	0
	bushings					0	0	0	0	0	0
	nuts					0	0	0	0	0	0
	pipe					0	0	0	0	0	0
	LB					0	0	0	0	0	0
	SLB					0	0	0	0	0	0
	chase nipple					0	0	0	0	0	0
	b					0	0	0	0	0	0
	c					0	0	0	0	0	0
	d					0	0	0	0	0	0
	e					0	0	0	0	0	0
	f					0	0	0	0	0	0
	g					0	0	0	0	0	0
	h					0	0	0	0	0	0
	I					0	0	0	0	0	0
	j					0	0	0	0	0	0

Panel A		Size	Quantity					1/2	3/4	1	1 1/4	1 1/2	2
	Connectors					0	0	0	0	0	0
	couplings					0	0	0	0	0	0
	bushings					0	0	0	0	0	0
	nuts					0	0	0	0	0	0
	pipe					0	0	0	0	0	0
	LB					0	0	0	0	0	0
	SLB					0	0	0	0	0	0
	chase nipple					0	0	0	0	0	0
	b					0	0	0	0	0	0
	c					0	0	0	0	0	0
	d					0	0	0	0	0	0
	e					0	0	0	0	0	0
	f					0	0	0	0	0	0
	g					0	0	0	0	0	0
	h					0	0	0	0	0	0
	I					0	0	0	0	0	0
	j					0	0	0	0	0	0

## Electrical List
Total Cost	$278.64
Cost Remaining	$-
						*
	Description	Manufacturer	Supplier	Part Number	Qty	Price	tax	Cost	O	R	Notes
Panels						$-	$-		*			$0.00
$278.64	Sub-panel, 100A, 1ph, lug, flush mount,	GE	CED		4	$64.65	$20.04	$278.64		*			$278.64
						$-	$-		*			$0.00
						$-	$-					$0.00
EMT Fittings						$-	$-					$0.00
$-						$-	$-					$0.00
	1/2", PVC, sweep					$2.00	$-	$-		*			$0.00
	1/2:, PVC, LB					$3.00	$-	$-		*			$0.00
						$-	$-		*			$0.00
	1-1/4", Connector with nut					$1.49	$-	$-		*			$0.00
	1-1/4", Coupling					$2.00	$-	$-		*			$0.00
	1-1/4", bushings					$0.50	$-	$-		*			$0.00
	1-1/4", chase nipples					$1.00	$-	$-		*			$0.00
	1-1/4", LB or pulling elbow					$7.00	$-	$-		*			$0.00
						$-	$-		*			$0.00
Conduit						$-	$-		*			$0.00
$-	1/2", PVC, 10'		Home Depot			$1.00	$-	$-		*			$0.00
	1/2", EMT, 10'					$-	$-		*			$0.00
	3/4", EMT, 10'					$-	$-		*			$0.00
	1-1/4", EMT, 10'					$5.00	$-	$-		*			$0.00
						$-	$-		*			$0.00
Wire						$-	$-		*			$0.00
$-	wire, copper, #2, blk, 500' roll					$183.75	$-	$-		*			$0.00
	wire, copper, #6, GRN, 500' roll					$76.80	$-	$-		*			$0.00
						$-	$-		*			$0.00
Breakers						$-	$-		*			$0.00
$-	30A, 2pl, 1 slot, GE					$10.87	$-	$-		*			$0.00
	50A, 2pl, 1 slot, GE					$10.87	$-	$-		*			$0.00
						$-	$-		*			$0.00
Misc						$-	$-		*			$0.00
$-						$-	$-		*			$0.00
	water bond clamps, hot water dielectrics					$4.00	$-	$-		*			$0.00
	lug, 3#6, bolt on					$5.00	$-	$-		*			$0.00
	lug, 2#6, bolt on					$2.00	$-	$-		*			$0.00
	ground bar, panel sized					$3.00	$-	$-		*			$0.00
	ground bar, 6#2, 1ph service panel,					$6.00	$-	$-		*			$0.00
	6x6x4 box, indoor					$15.00	$-	$-		*			$0.00
	Connector Block, 4 hole, 2 awg					$20.00	$-	$-					$0.00
	Connector Block, 2 hole, 2 awg					$15.00	$-	$-		*			$0.00
	hole covers, 1/2"					$0.15	$-	$-		*			$0.00
	hole covers, 3/4"					$0.25	$-	$-		*			$0.00
	6x6x4 box, outdoor					$15.00	$-	$-		*			$0.00
						$-	$-					$0.00
						$-	$-					$0.00
						$-	$-					$0.00
						$-	$-					$0.00
						$-	$-					$0.00
						$-	$-					$0.00
						$-	$-					$0.00
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-
						$-	$-

## Wire needs
	Wire Needed
		Size		BLK	WHT	GRN	BRE
		250	MCM	0
		1	AWG	0	0	0	0
		2	AWG	420	0	0	60
		4	AWG	0	0	0	0
		6	AWG	0	0	0	175
		8	AWG	48	0	0	0
		10	AWG	120	0	0	0
		12	AWG	0	0	0	0

	Cross Check	0
						823			0	0	0	0	0	420	0	0	60	0	0	0	0	0	0	0	175	48	0	0	0	120	0	0	0	0	0	0	0
Connections						250	1	1	1	1	2	2	2	2	4	4	4	4	6	6	6	6	8	8	8	8	10	10	10	10	12	12	12	12
	Description	Qty	Len	Size		Color	Type	Checked	Total Length			BLK	BLK	WHT	GRN	BRE	BLK	WHT	GRN	BRE	BLK	WHT	GRN	BRE	BLK	WHT	GRN	BRE	BLK	WHT	GRN	BRE	BLK	WHT	GRN	BRE	BLK	WHT	GRN	BRE
Panel 1, rear upstairs panel						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
	feed to new panel 1 from old end point	3	15	2		BLK	THHN		45			0	0	0	0	0	45	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
	Ground to new panel 1 from service	1	60	6		bre			60			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	60	0	0	0	0	0	0	0	0	0	0	0	0
						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
Panel 2, front upstairs panel						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
	feed to new panel 2 from service	3	25	2		blk	THHN		75			0	0	0	0	0	75	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
	Ground to new panel 2 from service	1	25	6		bre			25			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	25	0	0	0	0	0	0	0	0	0	0	0	0
						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
Panel A						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
	Panel ground to system ground point	1	10	6		BRE			10			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	10	0	0	0	0	0	0	0	0	0	0	0	0
						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
Panel B						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
	feeds from gutter to lugs	3	12	2		blk	THHN		36			0	0	0	0	0	36	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
	gutter ground point to panel	1	12	6		BRE			12			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	12	0	0	0	0	0	0	0	0	0	0	0	0
						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
Panel C						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
	Panel ground to gutter ground point	1	60	6		BRE	THHN		60			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	60	0	0	0	0	0	0	0	0	0	0	0	0
	feeds from gutter to lugs	4	60	2		blk			240			0	0	0	0	0	240	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
Panel D						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
	feeds from Panel C	3	8	2		blk	THHN		24			0	0	0	0	0	24	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
	ground from panel C	1	8	6		BRE			8			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	8	0	0	0	0	0	0	0	0	0	0	0	0
						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
Ufer	from service thru to water and gas bond	1	60	2		bre			60			0	0	0	0	0	0	0	0	60	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0
Hookups	splices to existing 50A services	6	8	8		blk			48			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	48	0	0	0	0	0	0	0	0	0	0	0
AC	feeds to ac	4	30	10		blk			120			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	120	0	0	0	0	0	0	0
						0			0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0	0

## Panels
Panel List
A	3 ph	outer shop	100 a	existing	12/24
B	3 ph	outer shop	100 a	new	12/24
C	3 ph	middle shop	100 a	new	12/24
D	3 ph	middle shop	100 a	new	12/24
1	3 ph	rear house	100 a	new	12/24
2	3 ph	front house	100 a	new	12/24

## Breakers
Panel A	3 ph	outer shop	Ampacity	Poles	Slots	In Stock
	1	Welder 1	100	3	3	Yes
	3
	5
	7	Welder 2		2	2	Yes
	9
	11
	2	outlet	30	3	3	Yes
	4
	6
	8
	10
	12

Panel B	3 ph	outer shop	Ampacity	Poles	Slots	In Stock
	1	lights	20	1	1	Yes
	3	outlets 1	20	1	1
	5	outlets 2	20	1	1
	7	exhaust fan	20	1	1
	9	Misc 1	20	1	1
	11	Misc 1	20	1	1
	2
	4
	6
	8
	10
	12

Panel C	3 ph	middle shop	Ampacity	Poles	Slots	In Stock
	1	Milling Machine	15	3	3	yes
	3
	5
	7	Air Compressor	20	1	1	Yes
	9
	11
	2	Sub Panel Feed	100	2	2	Yes
	4
	6	Lathe	20	3	3	yes
	8
	10
	12

Panel D	3 ph	middle shop	Ampacity	Poles	Slots	In Stock
	1	outlets	20	1	1	Yes
	3	lights	20	1	1
	5
	7
	9	misc 1	20	1	1	Yes
	11	misc 2	20	1	1
	2	misc 3	20	1	1
	4	misc 4	20	1	1
	6	misc 5	20	1	1
	8
	10
	12

Panel 1	3 ph	rear house	Ampacity	Poles	Slots	In Stock
	1	Air Conditioner	30	2	1	No

	3	Heater	50	2	1	No

	7	Water Heater	30	2	1	No

	9	Wall heater	20	1	1/2	Yes

	11	lights	20	1	1/2
		lights	20	1	1/2
	2	outlets	20	1	1/2
		outlets	20	1	1/2
	4	Misc 1	20	1	1/2
		Misc 2	20	1	1/2
	6	Misc 3	20	1	1/2
		Misc 4	20	1	1/2
	8			1
				1
	10

	12

Panel 2	3 ph	front house	Ampacity	Poles	Slots	In Stock
	1	Range	50	2	1	No

	3	Air Conditioner	30	2	1	Yes

	7	Heater	50	2	1

	9	Water Heater	30	2	1

	11	lights	20	1	1/2
		outlets	20	1	1/2
	2	bathroom	20	1	1/2
		kitchen 1	20	1	1/2
	4	Kitchen 2	20	1	1/2
		Misc	20	1	1/2
	6	Wall Heater	20	1	1/2

	8

	10

	12

## Stock Breakers
Ampacity	Poles	Slots	Stock on hand	Need for project	Purchase		Panel A	Panel B	Panel C	Panel D	Panel 1	Panel 2
15	1	1/2	0	0	0
15	2	2	0	0	0
15	3	3	1	1	0				1
20	1	1/2	23	17	0				1		9	7
20	1	1	13	13	0			6		7
20	2	1	0	0	0
20	2	2	0	0	0
20	3	3	2	1	0				1
30	1	1/2	2	0	0
30	2	1	1	4	3						2	2
30	3	3	1	1	0		1
50	1	1	2	0	0
50	2	1	1	3	2						1	2
60	2	2	1	0	0
100	2	2	4	2	0		1		1
100	3	3	1	1	0		1
				0	0
				0	0