N0TES
1. SMUD SERVICE SHALL INITIALLY BE 240V, 200A, 4 WIRE DELTA CONNECTED. SERVICE WILL CHANGE TO 208V, 200A, 4 WIRE WYE CONNECTION AT FUTURE DATE.
2. PER NOTE 1, “A” PHASE CONDUCTOR, ~200V , SHALL BE MARKED WITH ORANGE TAPE AND SHALL NOT BE USED FOR 120V CIRCUITS.
3. PER NOTE 1, ALL PANELBOARDS SHALL HAVE NAME PLATES NOTING SERVICE TYPE AND VOLTAGE. NAME PLATES SHALL BE UPDATED WHEN SERVICE CHANGES AT FUTURE DATE
4. ALL PANELBOARDS SHALL BE RATED FOR SPECIFIED VOLTAGE OR HIGHER
5. ALL ENCLOSURES SHALL BE RAIN PROOF, NEMA 3R
6. GFIC CIRCUIT BREAKERS SHALL BE USED ON BRANCH CIRCUITS WITH RECEPTACLES.
7. ALL RECEPTACLES SHALL BE EQUIPPED WITH IN-USE RAIN COVERS
8. FLOODLIGHTS (FL) WILL BE MOUNTED ON 21' 2” RIGID CONDUIT POLES ATTACHED TO BUILDING CONCRETE WALLS

FIXTURES
     FL FLOOD LIGHT 250W PSMH, 16” X 16” POLE MOUNT E-CONOLIGHT E-HR4P25QZ
     OL OUTDOOR LIGHT 23W CFL PAR 38 IN OUTDOOR LAMP HOLDER COMMERCIAL
     XL EXIT SIGN WITH LIGHT NEMA 4R LED EXIT SIGN WITH LIGHT, BATTERY GREENTORCH XWLC

LOAD CALCULATION
LOAD KVA DESCRIPTION
     4 KVA CONTINUOUS NON-MOTOR
     1.0 KVA 25% CONTINUOUS NON-MOTOR
     2 KVA NON-CONTINUOUS
   30 KVA RECEPTACLE (FIRST 10KVA)
   14.2 KVA RECEPTACLE (BALANCE AT 50%)
     0.5 KVA MOTOR LOAD
     0.1 KVA 25% OF LARGEST MOTOR
     0 KVA KITCHEN EQUIPMENT
     0 KVA HOTEL/MOTEL DEMAND
     0 KVA ARC WELDERS
     0 KVA RESISTANCE WELDERS
   51.8 LOAD KVA
 127.0 AMPS AT 240 V 3 PHASE